2-Engineering Scope

  - General Description

    - Scope of work description

    - Codes, Standards and Documents

    - Drawings

    - Materials and Equipment

    - Process Simulations and Design Calculations

  - job description

    - General

    - Detailed Scope of Work

    - Basic design review

- Process

- Instrumentation

- Electrical

- Mechanical

- Civil

- Pipelines

- General

    - Hazard and operability study (HAZOP).

    - Detail design.

  - field information and data

  - documentation

  - discrepancy

2-ENGINEERING SCOPE

  - General Description

    - Scope of work

This Scope of Work covers the minimum requirements for the basic/detail engineering and design of ARAB GAS PIPELINE PROJECT -PHASE  II.

The Contractor's Basic and Detailed engineering scope of work requires all the engineering Disciplines to hand safe and easy operable PROJECT within the contract time schedule including the supply of personnel, supervision, materials, computers, consumable and equipment to provide Basic and Detailed engineering for the PROJECT delivered complete to the COMPANY in accordance with this tender book RFQ Specifications and Standards and International Industry Codes and Standards.

CONTRACTOR shall undertake all detailed design and engineering calculations necessary to ensure that all aspects of the “ARAB GAS PIPELINE PROJECT -PHASE II “to satisfy the requirements of all RFQ, referenced code and standards stated in EXHIBIT (G)

CONTRACTOR shall supply one additional copy of all deliverables, drawings and documentation to the consultant with Which COMPANY shall be in contract to review, approve and supervise all activities of the project.

The name and address of the consultant shall be submitted to CONTRACTOR in the later stages.

The Basic and Detailed engineering works shall include but not limited to the , computer generated drawings and data designed by all the engineering Disciplines required for the 36 inch API 5L X70 Pipeline, Block Valve Stations, Emergency Shutdown Valves, Pig Receivers and Launchers station, vent system, flare system, drain system, fiscal  Metering Station(FMS),Gas Compressor units, Anchor Blocks ,control system, telecom system ,electrical system ,cathodic protection system ,other associated system like potable water and sewer systems and tie-in connections as follow:

-with ARAB GAS PIPELINE PROJECT - PHASE I  36” flange. at  BVS-6011.

-with ARAB GAS PIPELINE PROJECT - PHASE II-PART I  36” flange. at R-7003.

-with 36" inlet/outlet of the FMS & gas compressor.

for the  completely design of the PROJECT.

In addition to any other activities required by safe design and easy operation

As a minimum the Basic and Detail Engineering drawings and documentation shall be as per: AFPC Schedule-B, Engineering Documentation and Schedule PEA “Project Execution and Administration” (provided in Exhibit-F)

    - Codes, Standards and Documents

The Basic and Detailed engineering works shall be performed and carried out in accordance with all RFQ Specifications, Standards and International Industry Codes and Standards but not limited to that, described in the “EXHIBIT-G, Data References and Contract’s General Specifications”.

The CONTRACTOR shall be responsible for all Basic and Detailed engineering for all activities of the PROJECT including Field engineering and information data gathering.

    - Drawings

CADD Drawings shall be provided by the CONTRACTOR and are intended to show by means of symbols/text the location of all equipment that will be required for the PROJECT.

The CONTRACTOR shall provide detailed design engineering for the CADD generated Detailed Pipeline Alignment, P&ID and PFD, piping arrangement drawings etc.

The CONTRACTOR shall provide all CADD Drawings and its responsibility to show the all details of the work and to ensure the Drawings are correct and complete before beginning the work.

CADD Drawings shall include but are not limited to all pipeline engineering and typical crossing, Pipeline Alignment details, Block Valve Station and Shutdown Valve details, Scraper Launchers and Receivers details, Fiscals Metering Station (FMSs) details, Gas Compressor unit’s details, Instrument and Control details, Fiber Optic Cable and Telecommunication details, Electrical details, Cathodic Protection details and tie-in connecting details etc.

CONTRACTOR shall provide all the drawings as per the following procedure:

- 1st issue documents to be stamped "issued for review"

The COMPANY will review all engineering deliverables such as calculations, drawings, data sheets, specifications and other documents, which form part of CONTRACTOR’s supply.

- 2nd issue, to be stamped "approved for construction"

The CONTRACTOR shall revise and re-issue the calculations, drawings, data sheets, specifications and other documents which form part of the supply in accordance with all COMPANY’s comments.

- Final issue of drawings to be stamped "AS-BUILT"

The CONTRACTOR shall issue five (5) sets of construction drawings with complete legible red and blue mark-up reflecting the AS-BUILT installation in both hard copy and soft copy (On CD-ROM) using AutoCAD and other application software.

    - Materials and Equipment

The CONTRACTOR shall provide all personnel, tools, materials, computers and equipment to perform the Basic and Detailed engineering and design for the PROJECT in accordance with the Drawings, and General Specifications to meet the required overall completion date.

The CONTRACTOR shall perform all work in a professional workmanlike manner so as to present an accurate neat and finished package when completed.

This material shall be suitable for the design and operation parameters requirements

This material shall be completely suitable for the PROJECT environment.

    - Process Simulations and Design Calculations

The CONTRACTOR shall perform all the required computer process simulations and design calculations for the PROJECT in accordance with all RFQ Specifications and International Industry Codes and Standards.

  - job description

    - General

This job description covers the minimum requirements for the basic and detailed engineering of the PROJECT.

All works shall be done in accordance with RFQ Specifications and International Industry Codes and Standards.

    - Detailed Scope of Work

The Contractor's Basic and Detailed engineering works shall be performed by professional specialists that have the expertise to prepare computer generated drawings, equipment specifications, data sheets, detailed pipeline alignment drawings, calculations, requisitions and technical bid evaluations and carried out in accordance with all RFQ Specifications and International Industry Codes and Standards.

The CONTRACTOR engineering scope shall cover all the aspects included but not limited to these requested and described in EXHIBIT-B (scope of work)/section 1 general scope and definitions.

    - Basic design review

Upon completion of CONTRACTOR's "For Review" issue of Basic Design Package, COMPANY reserves the right to conduct a Basic Design Review.

The Basic Design Package will typically include but not limited to, the following:

- Process:

- PFD's and  P & ID's

- heat and material balances

- process model , process calculations and a summary of process

- Gas Compressor Calculations

- sizing calculations of all vessels

- flare/vent backpressure calculations (including all relief cases considered)

- flare/vent radiation calculations

- depressuring calculations

- cause and effect diagrams

- Instrumentation:

- P& ID's

- cause and effect diagrams

- functional logic diagrams

- EMCS and ESD systems architectural diagrams

- list of alarm and trip settings

- anti surge system

- Operating control& safeguarding philosophy

- Purchase orders/data sheets for:

          - EMCS system

          - ESD system

          - control valves

          - PSD/ESD valves (including depressuring valves)

          - relief valves

          - instrument gas system

- control room lay-out

- plot plans (main equipment and main cable routes)

- calculations for instrument gas usage, UPS requirements, control valves

- summary of instrumentation documentation and drawings

- Electrical:

- single line diagrams

- plot plan and cable routing drawings

- MCC building and switchgear lay-out

- Protection block diagram.

- the following calculations

          - system load flow calculations

          - short circuit calculations

          - one line diagram

- continuous and short circuit current carrying capacity of all electrical equipment

- multiplexer / de multiplexer equipment

- high voltage motor starting and run up time calculations

- utility data sheets

- mimic panel details

- annunciator panel details

- purchase order and data sheets for:

          - transformers

          - high voltage motors

          - DC supply units

          - high and low voltage switchgear

          - control and monitoring panel details

          - overhead lines

          - Fiber optic signaling system.

          - Solar system

- Mechanical:

- PFD's and P & ID's

- purchase orders/data sheets for:

          - all equipment

          - all rotating machine performance data and curves

          - inspection and test plans (per equipment)

          - all vessels

          - filters

          - Cyclone separator.

          - chemical injection packages if any

          - fuel/instrument gas package

          - the MCC building and control centre air conditioning requirements

- plot plans

- calculations for:

          - hydraulic study for the pipe line

          - rotating machine power calculations

          - the MCC building air conditioning

- Civil:

- plot plan/survey plan (including drainage plan)

- lay-out of the MCC building

- road drawings

- calculations for:

          - design/engineering MCC building and control centre

- Pipelines:

- proposed Gas  line, gas line routing

- pig launcher/receiver drawings

- P and ID's

- plot plans (showing entry and tie-ins)

- cathodic protection systems schematics

- location of corrosion monitoring points

- Gas trunk line hold up  calculations and purchase orders for:

          - pipeline, including coating for the trunk line

          - launchers/receivers

          - shut down and motorized valves

          - cathodic protection calculations

- General:

- Area classification.

- Design book

The design review shall be undertaken at location to be determined by CONTRACTOR and shall be undertaken by the Senior CONTRACTOR design engineers in conjunction with a review team from COMPANY.

    - Hazard and operability study (HAZOP).

On the basis of CONTRACTOR’s “For Approval” issue of P&ID, General Arrangement plans, Electrical Single Line diagrams, Instrument Cause & Effect Diagrams, Area Classification Drawings, and other applicable drawings, COMPANY will conduct a Hazard and Operability Study (HAZOP).

Contractor's key staff shall be made available to assist whenever requested.

Company's representative’s conduct off, or failure to conduct, or completion off, or failure to complete, such HAZOP shall not relieve CONTRACTOR from any of the responsibilities and obligations of this Contract.

After completion of HAZOP study, CONTRACTOR will be obliged to correct deficiencies revealed in the design at no cost or time impact to COMPANY

Company's approval of any activity and design shall not relieve CONTRACTOR from his responsibility to provide reliable, safe and easy operable PROJECT or to relieve him from his responsibilities and obligations of this contract.

The CONTRACTOR shall submit all the specification of the equipment and materials, they would supply, for COMPANY’s approval before procurement.

The CONTRACTOR shall allow Company's authorized representative(s) the opportunity for such review and comments before taking irreversible action or making monetary commitments with respect to purchase order, subcontract or, such like commitments.

The CONTRACTOR shall allow Company's authorized representative a comment period minimum of tow (2) weeks and shall respond to its comments, (if any); before taking further action with respect thereto.

Any activity required by the HAZOP and not include in the tender book scope of work will be a part of the project scope without any time or cost impact to the company

    - Detail design.

The Detail Design shall include but not limited to the following:

- Platform drawings

- Accessibility details

- Pipe support drawings and details

- Foundation drawing and re baring schedule

- Steel structural details and drawings

- Stress analysis

- Cable tray drawing and details

- Cable list and instrument list

- Instrument hook up drawing and details

- Loop drawings

- I/O list

- Heat tracing and insulation drawing and details.

- isometric drawing

- line list

- Any other typical drawings

COMPANY retains the right to comment on any detail design information.

The Basic/Detailed engineering scope of work shall cover as minimum all PROJECT parts described above of the following activities:

- Installing approximately 186 km of “36”API 5L X70 pipeline between Foreqls area and the Aleppo PRMS.

- Four (4) Block Valve Stations tagged as follow:

- BVS 6013.

- BVS 6014.

- BVS 6016.

- BVS 6017.

- ONE (1) Pig Launchers at ALFOREQLS FMS.

- ONE (1) Pig Receivers at R-7003 IN Aleppo PRMS.

- ONE (1) Pig Launchers at Intermediate station.

- ONE (1) Pig Receivers at Intermediate station.

- Three gas compressor units to be installed at Al Foreqls FMS, each compressor shall operate on 50% Max Flow rate (4 BCM). Contractor has to design the GCS on bases of tow compressors in operation and one stand by.

- Fiscal Metering Station (FMS) at Al Foreqls area with 4 BCM/Y capacity.

* Four tie-in: :

-with ARAB GAS PIPELINE PROJECT - PHASE I  36” flange. at  BVS-6011.

-with ARAB GAS PIPELINE PROJECT - PHASE II-PART I  36” flange. at R-7003.

-with 36" inlet/outlet of the FMS & gas compressor.

With related piping, material and equipments and all required system as described

hereunder but not limited to the following:

- Cathodic Protection System.

- Control/Monitoring, Telecommunication system with all data transforming and connecting with gas co-ordination center.

- Electrical system

- Any other activity required for the safe operability of the PROJECT.

To be handed over to the COMPANY safe and operable PROJECT as per these RFQ contained in this tender and international codes, standards and specification

  - field information and data

The CONTRACTOR is responsible for all Field Information and Data gathering to confirm that all the data and drawing provided from the COMPANY for the Basic and detailed engineering of the PROJECT are enough and correct.

So he is requested to arrange as required site visits with the COMPANY representatives co-ordination to make assurance that his required data are correct and there are no confusion or PROJECT misunderstanding will affect the PROJECT design and time completion.

  - documentation

# Scope

This scope describes the minimum requirements for information and data contained in the various documentation produced by the CONTRACTOR and / or his SUB-Contractors, vendors and manufacturers of equipment

# Standard Document Formats

COMPANY’s standards PROJECT documentation format shall be as stated in EXHIBIT-F / PEA unless otherwise defined in the RFQ.

Documents submitted in the format of a drawing with multiple sheets (such as instrument loop diagrams) shall consist of:

- a cover sheet

- index to the sheets submitted, including applicable revision numbers

- listing of symbols and abbreviations used

- detail sheets (as listed in the index)

- listing of tag numbers with reference to the relevant sheets

All drawings in a package shall have the same size and drawing number.

Drawing packages shall be prepared as a complete set for a facility or process unit.

Where more than one process unit is to be covered, a group of consecutive drawing numbers shall be used for the various sets of drawings.

Updated revisions shall be resubmitted immediately.

All revisions shall be clearly identified and include a description of the revision adjacent to the title box plus a ‘clouded’ boundary surrounding the revised areas with the revision number contained within a triangle located adjacent to the cloud.

Earlier revision clouds shall be removed unless contained on an existing "AS-BUILT" drawing supplied by the COMPANY.

# "AS-BUILT" Documentation

Following completion of commissioning, CONTRACTOR shall prepare final "AS-BUILT" drawings based on the "red-and-blue" marked-up drawing maintained during construction and commissioning which reviewed and accepted by the COMPANY.

CONTRACTOR shall be fully responsible for the accuracy of the "AS-BUILT" deliverables.

All "AS-BUILT" drawings shall be noted with a new revision number, including those which do not require modification from the previous revision.

All revision clouds and triangles pertaining to previous revisions shall be removed from the AS-BUILT revision.

One set of "red-and-blue" mark-ups of all documents and drawings shall be provided to COMPANY prior to the planned date of introduction of process media.

# Manuals

Manuals shall be sized and formatted according to the requirements of

EXHIBIT-F/ PEA with clear subdivisions placed in logical system and equipment sections.

Data shall be specific to equipment installed.

Generic information will be rejected.

Indexing shall include both equipment names and tag numbers.

A full index shall be contained in each volume of the manual.

All documents shall have sufficient left-hand margin (gutter) to easily read the complete document.

A complete set of CONTRACT submitted documents (drawings, data sheets, calculations, certification etc.) shall be contained in the manuals as well as manufacturers’ data, drawings, operational information, maintenance instructions, procedures, special tools etc. necessary to fully understand the reliable operation of plant and equipment for the specified operating duties.

Separate manufacturer’s manuals are permitted if their size will not sensibly allow for integration within the CONTRACTORs PROJECT manuals.

Clear cross-referencing shall be indicated. CONTRACTOR will be responsible for information contained within manufacturer’s manuals and the submission of revisions or updates.

# Symbols and units

Symbols used on drawings shall comply with:

- IEC 617 for electrical drawings

- ISA S5.1 for instrumentation drawings

- BS 1553 for mechanical drawings

For symbols not covered by the above standards, diagrams shall use symbols as shown on COMPANY’s legend sheets According to appendix 2 of PEA.

For all units of measurement, the SI system shall be followed according to appendix 1 of PEA.

# Instrument Design Software

CONTRACTOR shall confirm with his bid which Computer Aided engineering (CAE) package will be used for instrumentation design.

CONTRACTOR shall submit his standard templates and examples of instrumentation drawings as identified by this scope, showing typical level of details, to COMPANY for review prior to commencing the design.

# Drawing, diagrams and schematics

All drawing, diagrams and schematics in addition to the manuals shall be according to AFPC / SCHEDULE- B

  - discrepancy

In case a discrepancy arises or exists between codes, standards, drawings and documents, the most severe shall govern in the following priority:

- RFQ tender documents

- (AFPC)  scopes and specifications

- International industry codes and standards