6 - ELECTRICAL SCOPE

6.1	GENERAL DESCRIPTION

6.2	JOB DESCRIPTION

6.3	ELECTRICAL EQUIPMENT

6.4	TESTING, COMMISSIONING AND START-UP

6.5	FIELD INSPECTION

6.6	ELECTRICAL DRAWING LIST

6 - ELECTRICAL SCOPE

6.1	GENERAL DESCRIPTION

6.1.1	Scope

This Scope of Work covers the minimum electrical requirements for Arab Gas Pipeline project-phaseII. CONTRACTOR shall provide engineering, procurement, personnel, supervision, materials, consumable, construction and commissioning to deliver the complete electrical works for this project to the COMPANY in accordance with RFQ Specifications and Standards and Industry Codes and Standards. The Scope of Work includes but is not limited to all-electrical works and work sites required.

6.1.2	Codes, Standards and Documents

The electrical system, including equipment, design and installation shall conform to all applicable RFQ specifications and schedules, United States and International Codes and Standards including but not limited to that specified in the “EXHIBIT-G, Data References and Contract’s General Specifications”.

In case a discrepancy arises or exists between codes, standards, drawings and documents, the most severe shall govern.

CONTRACTOR shall be responsible for obtaining all necessary permits to complete the  work.

6.1.3	Drawings

CONTRACTOR shall provide all the drawings and is responsible to show all the details of the work and to ensure the drawings are correct and complete before beginning the work.

The work shall include but not be limited to the location and function of all electrical equipment including the diesel stand-by generator, connecting with additional power sources and electrical distribution and wiring system.

By "As-Built", it means that the CONTRACTOR has adequately shown, or provided additional sketches, to clearly convey the information for the following items as minimum:

-	Device and equipment locations

-	All junction box wiring changes, including terminal strip layout

-	All stand-by generator schematic changes

-	All control panel layout and schematic changes

- All wires not identified on the schematics, which were field assigned tagging.

6.1.4	Materials and Products

CONTRACTOR shall provide all materials, personnel, tools and construction equipment for the electrical installation requirements of the facilities in accordance with Drawings, General Specifications, Codes and Standards.

6.1.5	Construction

CONTRACTOR shall provide all personnel supervision, co-ordination, tools and materials as well as competent knowledge of construction for the installation, testing and putting into operation of each electrical system, diesel stand-by generator system and product specified

CONTRACTOR shall execute all work in a workmanlike manner so as to present a neat and finished appearance when completed. CONTRACTOR to maintain his works area neat and clean, by removing garbage into the proper bins.

CONTRACTOR shall become familiar with the Construction Drawings of all trades and when laying out the work with regard to structural, piping and mechanical features.

CONTRACTOR shall perform the commissioning and start-up activities to the satisfaction of the COMPANY or its representatives.

6.2	JOB DESCRIPTION

6.2.1	General

This job description covers the basic requirements for the installation of electrical equipment and materials.

CONTRACTOR shall procure, supply and provide all materials, personnel, tools and construction equipment for the installation of the electrical works.

Plant areas are classified for selection and installation of electrical equipment and material as required by the National Electrical Code (NEC) or equivalent. Installation and wiring of electrical equipment shall be approved for the areas in which the equipment is installed.

6.2.2	Detailed Scope of Work

CONTRACTOR shall perform, but not be limited to, the following work as per RFQ specifications and standards

Supply and install dual type in line UPS systems including charger, inverters and batteries for four (4) hours continuous operation of the station to cover the requirement of control system, , fire and gas Detection system and emergency lights for the Fiscal Metering Station (FMS) Including gas compressor units (at AL FOREQLS), and (48)hours for telecommunication System.

Supply and install, dual type in line UPS system, including charger, inverters and batteries for forty- eight (48) hours, to cover the requirement of control system, telecommunication system, and emergency lights for all Block Valve Stations, which are powered from overhead power line.

CONTRACTOR shall wire all end devices to the required panel(s).

Supply and install conductors from the diesel stand-by generator to the switchgear and bus ducts to the control center panel of FMS's and gas compressor units (at AL FOREQLS).

Supply and install all electrical materials and wiring in buildings, including lighting, socket outlet and heating Conduit to be concealed outside building walls.

Supply and install feeders to buildings, equipment skids and other areas for lighting, heating and heat tracing, process and power loads.

Supply and install wiring outlets, junction boxes and make all connections to supplied devices.

Supply and install all lighting fixture controls and make lighting system functional and install automatic circuit breakers with photo cells in the BVS's

Supply and install pipeline and facilities earthing, and lightning protection systems.

Supply and install complete sets of conduits, equipment as required to give an acceptable job.

Supply and install cable tray system, cable tray support brackets as required to give an acceptable job. CONTRACTOR to provide covers on all cable trays.

Provide all ditching, protective covering plastic cable markers and back fill for underground cable runs. Install marker posts to identify cable underground location and crossings.

Install and connect power supply from the 20 kV Syrian overhead power lines for:

approximately 186 km of “36”API 5L X70 pipeline between FOREQLS area and the Syrian /Turkish border.

- Four (4) Block Valve Stations.

- Launcher at Al FOREQLS area, end of Arab gas pipe line Phase I .

- Receiver at R-7003 in Aleppo PRMS.

- Intermediate station S-6015.

- Fiscal Metering Station ( FMS ) at Al FOREQLS area with 4 BCM capacity:

- Compressor units at Al FOREQLS area with  capacity  4 BCM

by installing 20/0.4 kV transformers, all power cable required with posts. The transformer shall be (50) kVA for each BVSs.

Contractor shall also provide in his price list, the unit price for all the electrical equipment needed to be installed in each mentioned locations, which shall be powered from overhead power line (including unit price of 1 km cable, transformer, electrical posts etc.)

However the Contractor’s lump sum price shall include the cost of supply and installation of five electrical power system to be installed in BVSs and intermediate stations, which shall be powered from over head power line including (( 7  ) of 20/0.4 kV transformers and 15   km of overhead power cable with required posts to feed electric supply to the above mention locations.

-The Fiscal Metering Station (FMS) and Compressor units shall be powered from the following electric sources:

1-	Supply and install stand-by diesel generator designed for 125% full load of FMS and Compressor units, requirement furnished with diesel tank sufficient for one-week operation and all necessary protection devices and control panel. Diesel generator shall be installed under the sunshade and automatically shall be in line during main power shut off .

2-	Connect power supply from the 20 kV Syrian overhead power line near the FMS and Compressor units, and install 20/0.4 kV transformer sized for 125% of maximum station load requirement. Contractor shall supply all materials for this activity.

Supply and install as minimum eight (8) electric lighting posts will be articulating at (FMS) and Compressor units area with Sodium Vapor lamps of 1000 W with control panels to provide sufficient illumination level as per RFQ standards and requirement. This is Contractor responsibility to confirm the sufficient illumination level in the area as per specification and standards.

All skid lighting shall use 150 W lamps of sodium vapor type.

Supply and install all other miscellaneous items required to complete the job.

Supply and install air conditioning units/ wall mounted (split type, cooling& heating)/ for all rooms in FMS's, all BVSs and stations powered from overhead power lines

Supply and install interphone system in the FMS and Compressor units area with eight (8) lines and phone sets to enable Control room’s Operators talking with Operators in process area and be suitable for classified area.

6.3	ELECTRICAL EQUIPMENT

The major electrical equipment and works required for the electrical system for all project location and facilities (as applicable) shall include, but not be limited to, the following:

-	Power Supply Connections from: overhead power line, emergency diesel generator.

-	Distribution panel, switchgear and Control Center Panel

-	Instrumentation and Emergency Power Supplies including Inverter, Battery charger and Batteries (220V and 24 VDC- UPS System).

-	Power, Control and Instrumentation Cabling and Cable Tray System

-	Earthing and Supplementary bonding lightning protection

-	Building Services including Heating, Air Conditioning, and Ventilation Equipment, Lighting and Socket Outlet Installation.

- Electric power supply either from the overhead power line for all BVSs stations.

- Flood lighting fixture, and skid lighting.

CONTRACTOR shall supply all materials and products required to complete the project as per RFQ specification, codes and standards.

6.4	TESTING, COMMISSIONING AND START-UP

6.4.1	Testing

CONTRACTOR shall supply all equipment and personnel required for testing. Testing shall be done in the presence of the COMPANY's representative and electrical inspection authority.

Testing on the electrical system shall include, but not be limited to, the following major components:

- Testing and Verification of Diesel Stand-by Generator Output Voltages at:

- Normal Load and

- Maximum Load

-	Verification of Voltages at all levels (380/220 VAC, 24 VDC etc.)

-	Facilities Earthing System

-	Megger all power cables

-	Continuity tests of all control cables

-	High potential test

All results of tests and readings shall be recorded, documented and certified.

6.4.2	Commissioning and Start-up

CONTRACTOR shall provide sufficient manpower for the duration of the commissioning and start-up period.  The CONTRACTOR shall be aware that the commissioning period is the time required to check wiring and control systems and make corrections as required making the system READY FOR START-UP. The start-up period is the time after commissioning to put the Facility(s) into continuous operation.

CONTRACTOR shall accept the direction and advice of the COMPANY’s representative in all areas of commissioning.

6.5	FIELD INSPECTION

Inspection of the works and activities shall be as per general requirement specified in the section 1-General Scope and Definitions.

Inspection shall not relieve CONTRACTOR from any duties, obligations, responsibilities or liabilities under this Construction Agreement.

6.6	ELECTRICAL DRAWING & SPECIFICATION LISTS

All Drawings and specification lists and equipment data sheets, shall be provided by CONTRACTOR