SPS-9	Specification of Instrumentation

SCHEDULE SPS-9

PROJECT SPECIFICATION FOR INSTRUMENTATION

TABLE OF CONTENTS

1.0	SCOPE.

2.0	GENERAL

3.0	PRESSURE REDUCTION/METERING STATIONS.

4.0	BLOCK VALVE STATIONS.

5.0	TELEMETERY / TELECONTROL.

1.0	SCOPE.

This specification is intended to define the minimum requirements for the instrumentation and control for the Arab Gas Pipeline project Phase II.

2.0	GENERAL

2.1	The design and supply of instruments and controls shall be in accordance with RFQ Specification, Schedule L unless otherwise specified in the functional specifications provided for this project.

Note that with the use of instrument gas as power supply; all materials shall be in accordance with section 1.5.3 of Schedule L.

2.2	All instruments and controls associated with the flow computing and pressure controlling must be electronic and shall be of smart type devices. Pressure transmitters shall be used for shutdown (ESD) purposes.

2.3	All electrical instruments and controls must be powered by 24 VDC, supplied from a dual DC, UPS system consisting of two chargers and two battery banks, in accordance with Schedule F. Battery autonomy must be as further specified in the RFQ documents.

2.4	Electrical analog signals shall be 4-20 MA.

2.5	Instruments installed in hazardous areas shall be certified accordingly. Contractor shall make available certificates issued by an internationally recognized testing authority. For all circuits (e.g. analog circuits, on/off power, etc) explosion proof (EExd) is required.

3.0	FMS's.

  - Contractor shall make available sizing and calculations for the various conditions

In order to review and approve by COMPANY.

3.2	For Gas flow measurements, flow measurement shall be made by using of Ultrasonic Technologies according to (AGA-9).

3.5 	controllers, indications, alarms etc shall be installed in the control cabinet located in the control room of FMS's buildings which shall be in a safe distance from the process.

3.6	For the ESD system, refer functional specification SPS-5.

3.7	Local panels, if used, must conform to Schedule L, except as follows:

-	The hem must be electric (explosion proof).

-	Over-ride switches for slam-shut valve pressure control sensors must be located in boxes in the back of the panels.

-	The panel doors must be provided with locks.

-	All components must conform to Section 1.5.3 of Schedule L.

-	Panels must be vented to atmosphere utilizing flame inhibitors.

All instrument vents must be piped outside of the panels.

- BLOCK VALVE STATIONS.

The limit switches and pressure switches and transmitters  on each block valve shall be explosion proof (EExd) and connected to the cabinet installed in the nearby telecommunication building which is safe by virtue of its distance from gas sources.

5.0	TELEMETERY / TELECONTROL.

5.1	Telemetry shall be provided for remote indication and remote control.

5.2	Signals to be transmitted to the control rooms at FMS's and interfaced to GCC SCADA system, but not limited to:

5.2.1	Block Valve Stations:

- 	Valve open/close status.

-	System failures.

-	Doors (valve, batteries, control) buildings open alarm.

-	Battery, Charger and Inverter status.

-		Line Break Detection signal

-	Line pressure down stream of the main valve.

-	Smock and heat detectors signals.

5.2.2	Launchers/Receivers:

-Pig launched and received of all

Pigging facilities.

-Pressure and temperature data of the line in the pigging

-Facilities at Launcher / Receiver areas.

5.2.3	FMS's:

For each metering stream including I/G unit:

-	Gas pressure at meter inlet.

-	Gas temperature at meter inlet.

-	Actual and corrected flow rate.

-	Actual and corrected total volume.

-	Differential pressure.

    - gas compressor station:

-all parameters of the compressor and gas turbine.

-all valves status.

-system failure.

For station:

Open/close position of shutdown valves.

Gas density

Common gas temperature inlet

Common gas pressure at inlet

Common shutdown alarms.

System failures.

Common pre-alarms.

Common override alarms.

  - Remote controls shall be provided to each block valve station so that in the event of closing    such block valve in case of line break was detected, the block valves upstream and downstream of the closed valve will be automatically closed.

6.0-All HAZOP study result and requirements should be integrated in the design without any time and/or cost impact to COMPANY.

7.0-Contractor shall provide all special tools for the delivered equipments for programming /test and maintenance.

8.0-Contractor is responsible for any software\hardware required to fulfill system communication and SCADA signal transmitting.

9.0-All proposed DCS equipments and software should be proven (high) reliability and utilize standard software and hardware.

10.0-The system software shall be of the latest proven international release at the time of factory acceptance testing (FAT).

11.0-DCS vendor shall ensure that overall system integrity is main tined and communication between the various modes and sub-system is not overloaded.

12.0- the contractor is responsible to provide all necessary licenses for the applied software (operation and SCADA)

13.0-Programmable logic controllers (PLC's) shall control separately each gas compressor units.

14.0-A common DCS system shall be installed at control room for controlling of all equipment of FMS including the compressor units.

15.0-the contractor shall be responsible to transmit all DATA/SIGNALS from PLC of GCU's to Station control room and GCC.

16.0-the contractor shall be responsible to provide all instrument special tools for operating, check and maintenance purpose for all FMS's equipment.