SCHEDULE SPS-11

PROJECT SPECIFICATION FOR FIBER OPTIC CABLE

TABLE OF CONTENTS

1.0	SCOPE.

2.0	CODES AND STANDARDS

3.0	GENERAL

4.0	OPTICAL FIBER

5.0	SECONDARY COATING

6.0	STRENGTH MEMBER

7.0	STRANDING

8.0	FILLING

9.0	CORE COVERING

10.0	MOISTURE BARRIER SHEATH

11.0	ARMOUR

12.0	OUTER SHEATH

13.0	IDENTIFICATION

14.0	CABLE SIZES

15.0	OPTICAL REQUIREMENTS

16.0	MECHANICAL REQUIRMENTS

17.0	MANUFACTURERS TEST RESULTS

18.0	CABLE ENDS

19.0	DELIVERY

20.0     SPECIFICATION

1.0 	SCOPE:

This specification is intended to define the minimum requirements for the supply of 24 cores fiber optic cable for voice and data communication of the ARAB GAS PIPE LINE -   PHASE II.

If CONTRACTOR offers cable, which does not comply fully with the specification, then he shall clearly state any variations and provide justification for the variations.

Because, of the operation of the fiber optic cable in close proximity to an impressed Cathodic protection system on the pipeline and its traversing of areas of high earth resistance subjected to lightning activity. The CONTRACTOR shall clearly define how he proposes to install the cable armor sheathing and the earthing arrangements at each BVS - FMS LOUNCGER, RECIVER, INTERMEDIATE STATION.

2.0	CODES AND STANDARDS:

The cable shall be fully in compliance with latest CCITT recommendations.

3.0	GENERAL:

3.1	The present specification specifies the fibers to be of the single-mode type.

3.2	The cable route, for which this specification applies, is along the ARAB GAS PIPE LINE -PHASE II, it is the Contractor’s responsibility, to deliver and install the required quantity of the cable to be laid between both Gas Coordination Center and all BVS,S – FMS  without any increasing/ decreasing of Lump Sum prices as turnkey based job

3.3	This specification covers requirements for filled optical fiber cables, for direct buried applications.

The fibers are of the single-mode type, which are having a loose secondary coating of high modulus plastic. The tubes are filled with a filling compound.

The center of the core contains a metallic strength member.

The tubes, with fibers, are stranded around the strength member, a compact and circular cable core.

The cable structure is completed by application of suitable core wrapping and APL (Aluminum Polyethylene Laminate) inner sheath. Over the APL sheath two layers of steel tape shall be applied.

A polyethylene outer jacket shall complete the cable.

4.0	OPTICAL FIBER

4.1	Each optical fiber consists of a single-mode type, according to CCITT recommendation G 652, and made of high-grade silica materials.

4.2	Geometrical Values

The nominal mode field diameter shall be 9-10 micron at 1550 nm.

Mode field diameter deviation:	125 - micron.

Cladding diameter			equal or less than 1 micron.

Cladding on circularity		less than 2%.

Crush                                                   50 DA n/cm

Water penetration                                1m

4.3	The primary coating consists of a double layer UV-cured acrylate.

The coating diameter shall be 250 plus or minus 15 micron.

5.0	SECONDARY COATING:

The jacket of each fiber shall be a tube of high modulus plastic.

Reclaimed material shall not be used.

The inside diameter of the tube shall be 1.0 mm nominal.

The outside diameter of the tube shall be 1.5 mm nominal.

Each tube shall be filled with a filling compound consisting of fumed silica dispersed in oil to prevent water ingress and to ensure low stress levels of the fiber.

6.0	STRENGTH MEMBER:

The center of the core contains strength of steel with a nominal diameter of 1.5 mm.

7.0	STRANDING:

Four jacketed optical fibers and two PE fillers are stranded around the strength member and sealed with hot melt.

The identification of the cable shall be as follows:

The sequence of counting the filler and fiber coatings shall be in anti-clockwise direction, seen at the running end of the cable.

Colors of the PE fillers shall correspond reasonable with the standard colors shown in IEC publication 304.

8.0	FILLING:

The interstices between secondary coating, strength member and core wrapping shall be filled with jelly to prevent axial and longitudinal flow of water and/or soluble chemicals throughout the cable.

8.1	Filling Compound Properties:

The filling compound shall not have any harmful effect upon the other materials of which the cable is made and shall not change or blur the colors of the fiber tubes.

The filling compound shall be free from dirt, metallic particles and other foreign materials.

8.1.1	The drop point shall not be less than +80 degree c. when tested in accordance with testing method IP 132.

8.1.2	The flash point shall not be less than +175 degree c. testing method ASTM D93.

8.1.3	There shall be no separation of the constituents forming the compound.

9.0	CORE COVERING:

A wrapping or wrappings of non-hygroscope tape of other approved material shall be applied over the cable core.

The wrapping may be applied helically or longitudinally with an overlap.

10.0	MOISTURE BARRIER SHEATH:

10.1	To prevent moisture ingress the cable core shall be completely covered with a plastic coated aluminum coil, applied longitudinally with an overlap of at least 3mm.

Over this foil a polyethylene inner sheath shall be extruded which shall be bonded to the plastic coated aluminum foil. The thickness of the inner sheath shall be nominal 1.0 mm.

10.2.	Metallic Foil:

The aluminum foil shall have a thickness of 0.15 mm + 0.025 mm. And shall be coated at both sides with a protective plastic coating.

The thickness of the protective coating shall be at least 0.03 mm.

The aluminum foil shall be electrically continuous throughout the cable length.

10.3	Peel Strength of Aluminum Foil on Sheath:

The polyethylene sheath shall fuse with the aluminum foil. The peek strength of the polyethylene sheath on the aluminum foil shall be not less than 20 N per 25 mm.

Polyethylene Inner Sheath:

The sheath shall consist of a tough weather resistant, high molecular weight polyethylene compound meeting the requirements of ASTM D 1248, Type I, Class C, Category 5, and Grade J3.

The sheath shall be circular, free form pinholes, joints, mended places and other defects.

The average thickness at any cross section shall not be less than 90% of the specified thickness. The minimum spot thickness shall be not less than 80% of the specified thickness.

11.0	ARMOR:

11.1	Steel Tape Armor:

11.1.1	The armor consists of two layers of galvanized soft steel tape with a nominal thickness of 0.2 mm.

11.1.2	The two layers shall be laid helically in the same direction, so that the outer tape is approximately central over the gap of the inner tape.

The gap between adjacent turns of each tape shall not exceed 50% of the width of the tape.

The outer tape shall overlap the inner tape on both sides by not less than 15% of the tape width.

11.1.3	The steel tapes shall have a tensile performance of 300-450 N/mm.

The weight of his zinc coating on each side shall not be less tan 60 gr/m2.

12.0	OUTER SHEATH:

12.1	The sheath shall consist of a tough weather resistant, high molecular weight polyethylene compound meeting the requirements of ASTM D 1248, type III, Class C, Category 5, and Grade J3.

12.2	The sheath shall be circular, free from pinholes, joints, mended places and other defects.

12.3	The nominal thickness of the outer sheath shall be 2.0 mm.

12.4	The average thickness of any cross section shall not be less than 90% of the specified thickness.

The minimum spot thick-ness shall not be less than 80% of the specified thickness.

13.0	IDENTIFICATION

Identification shall be printed or embossed on the outer sheath with the following inscription:

1.	Arrow

2.	Manufacturer’s Name

3.	Year of Manufacturing

4.	Optical Cable.

14.0	CABLE SIZES:

Nominal cable diameter 			12.5 mm.

Nominal thickness outer sheaths 		2.0 mm.

15.0	OPTICAL REQUIREMENTS:

1550 nm optical fiber cable (standard specification).

Attenuation coefficient 1550nm	< 0.22 db/km

Dispersion			Maximum	      3.5 ps / nm. Km

Mode field			Nominal 9-10 micron.

Tolerance = 10%.

Cut-off wavelength		1100-1280 nm.

* Typical values of cable parameters shall be the average value of all fibers in the cable allocated of particular repeater secant.

16.0	MECHNIACL REQUIREMENTS:

Temperature range	 	Transport, storage and operation (-30 to 70) degree c.

Installation (-100 to + 50) degree C.

Maximum pulling forces	1200 N.

Minimum bending radius	during installation: 19x cable diameter.

After lying: 10x-cable diameter.

Nominal cable diameter:	12.5 mm.

Standard lengths:	2100 / 4200 mm.

Length tolerance	+ 5%, maximum 100 m.

17.0	MANUFACUTRERS TEST RESULTS:

17.1	Testing is based on a quality assurance system, comprising quality control procedures, which ensure that the product meets the specified requirements.

Final testing of cables shall be done on each cable length for attenuation measurements and on a random basis for standard mechanical, physical and visual tests. Typical tests, such as but not limited to tensile performance, crush resistance, repeated bending, cable bend, etc. Do not form part of standard routine measurements.

17.2	Test Certificates:

The purchaser has the right to call for schedules of all measurements carried out, and to check the test results. Summary of certified test record shall be provided upon requests.

17.3	Inspection:

If inspection of above test result should be required, shall be carried out by third party, such parties shall be nominated and paid by the Purchaser. Inspection procedures to be agreed upon.

18.0	CABLE ENDS:

To prevent ingress of moisture the cable ends shall be sealed with shrinkable caps.

19.0	DELIVERY:

19.1	The cable shall be delivered in lengths, as specified in par. 16.0 on strong wooden drums with close fitting battens.

Deviation Drum Lengths:

The drum length may deviate by maximum + 100 m of the nominal drum length.

Maximum 10% of the drums to be supplied may have a shorter length.

The minimum drum length shall be not less than 400 m.

19.2	The barrel diameter of the drum shall not be less than 38 times the diameter of the cable to be wound thereon.

19.3	All timber used for drum construction and battening shall be rot proof.

19.4	The cable shall be tightly coiled on the drum and the ends effectively secured to prevent movement during transport and handling.

19.5	A distinguishable number and the following items shall be plainly marked on the outside of at least one flange of each drum:

a.	Order number.

b.	Manufacturer’s name

c.	Identification of cable type, number of fibers

d.	Net and gross weight

e.	Length in meters

f.	Each flange shall carry an arrow indelibly applied to denote the direction of rolling (i.e. in opposite direction to that in, which the outer end of the cable points).

20.0	SPECIFICATION REFERRED TO:

ASTM D 93

ASTM D 1248

CCITT G 652

IEC 304

IP 132

ITU-T G652