SPS-7	Specification of Control Cabinet

SCHEDULE SPS-7

PROJECT SPECIFICATION FOR CONTROL CABINETS

TABLE OF CONTENTS

1.0	SCOPE.

2.0	GENERAL.

3.0	CONTROL CABINET.

1.0	SCOPE.

This specification is intended to define the minimum requirements for the design of control cabinets for the Arab Gas Pipeline project Phase II.

2.0	GENERAL

2.1	The control cabinets shall be installed in a metering building located at the FMS's, compressor unit's area and in BVS buildings.

2.2.	The metering buildings shall be located in safe area.

2.3	The control cabinets shall be used for control, indication, alarm annunciation and shutdown of the FMS's and BVS's.

Instruments and controls to be installed are at least,

-	Push buttons.

-	Counters, indicators.

-	Alarm enunciator.

-	Logic.

-	ESD system.

-	Controllers (if any).

-	Auxiliaries.

3.0	Control Cabinet specifications

3.1	The control cabinets shall be constructed as a freestanding, self-supporting, single lift unit.

3.2 	Lifting lugs at suitable positions are to be provided.

3.3	Lift-off type doors shall be provided with t-type handle, cylinder lock and ventilation louvers.

Doors to be located at the rear of the cabinet.

3.4	The outside color of the cabinets is to be colored light Grey. The inside is to be colored blanch white.

3.5	All display instruments shall be flush mounted on the front of the cabinet.

3.6	All internal wiring shall be flexible stranding copper wire, with a minimum size of 18 AWG.

Wires shall be marked at all terminations with a wire number. Wire markers shall be sleeve type PVC wire markers that resist oil, grease,

Acid and abrasion. Wraps around markers held by adhesive are not acceptable.

3.7	Wiring shall be laid in PVC ducting with covering lid. Wiring, terminals and ducting shall be standard colored.

3.8	Instrumentation insulated tinned copper earth bus bars, size 4 x 12 mm shall be incorporated in the cabinets to be used for earthing cable screens.

Bars to be provided with M6 tinned copper screw at 20-mm intervals, each with washer.

An earthing boss suitable for earth wire size no.6 AWG shall be provided inside the cabinets and easy accessible.

Doors shall be earthen by means of a flexible copper connection.

3.9	Instruments and controls shall operate on 24 VDC.

3.10	All powered outputs shall have fused terminals.

Outputs for solenoid shall have diodes in parallel for break spark reduction.

3.11	The 24 VDC supply lines shall be connected to a double pole circuit breaker.

Each group of supply shall have its own circuit breaker.

The distribution panel shall have selective protection.