SPS-8	Specification of Orifice Meter Runs

SCHEDULE SPS-8

PROJECT SPECIFICATION FOR ORIFICE METER RUNS

TABLE OF CONTENTS

1.0	SCOPE.

2.0	CODES, STANDARDS, AND COMPANY’s SPECIFICATIONS.

3.0	METER RUN ASSEMBLY.

1.0	SCOPE.

This specification is intended to define the minimum requirements for the design and fabrication of orifice meter runs for Arab Gas Pipeline project Phase II.

2.0	CODES, STANDARDS AND COMPANY’s SPECIFICATIONS.

Design and fabrication of the orifice meter runs shall be in accordance with:

-	International standard 		ISO 5167 latest edition.

-	Company Specifications.	EXHIBIT-G.

3.0	METER RUN ASSEMBLY.

3.1	Each orifice meter run shall include:

-	One orifice fitting (under pressure retractable).

-	Straight length of pipe as specified below.

-	Installation, with metal covers, to cover the upstream straight length of pipe work.

-	One thermowell with 4 wires Pt100 resistance temperature detector.

-	One smart type pressure transmitter.

-	Three smart type differential pressure transmitters.

3.2	To meet site requirements and ISO 5167 the upstream straight length of pipe work shall be 32 D long and the minimum downstream straight length of pipe work shall be 7 D long.

(D = mean the bore diameter of the pipe).

3.3	Temperature measurement shall be upstream of the orifice plate at a distance of 31 D from the orifice plate.

3.4	Static pressure shall be measured in the plane of the upstream pressure tapping.

3.5	The orifice fitting shall be supplied from the manufacturer of the orifice plate holder with 10 D of upstream pipe attached to ISO 5167 requirements and 7 D of downstream pipe attached to ISO 5167 requirements.

The free end of the upstream length must be finished for welding a further upstream length to it. The downstream straight length must be finished with a welding neck, raised face, flange.

3.6	To complete the straight length requirement of 32D upstream, a loose meter tube with a minimum length of 22D shall be provided and shall be clearly marked with flow direction and referenced meter run.

3.7	The circularity and uniformity of bore of the orifice meter’s straight length shall be according to ISO 5167.

3.8	The orifice fitting shall be the Daniel Senior (or equivalent) Welding Neck type, with flange tapping with isolation valves welded to the fitting nozzles (as specified within Schedule L). Actual pipe bore, measured in accordance with ISO 5167, shall be stamped on the orifice carrier body. All tube fittings shall be SS Swage lock or equivalent.

3.9	Each orifice fitting shall be supplied with two orifice plates for each beta ratio. The bores shall be for beta = 0.3, 0.4, 0.5 and 0.6.

Each plate shall be separately packed and supplied with a certified measuring report as evidence that Contractor shall prepare calculations for each orifice bore.

3.10	The sizing of the meter runs shall be such that the maximum flow rate for the location can be accommodated with an orifice beta ratio no larger than 0.55 and a high range differential pressure transmitter with a range of 500 mbar.

CONTRACTOR shall confirm meter run sizes to meet this requirement.

3.11.	Meter runs shall be supplied from a single manufacturer. The unit shall be certified and a copy of the certification submitted to COMPANY.

3.12	A permanently attached SS tag, listing manufacturer’s name and address, the unit’s model number and serial number shall identify meter runs.

3.13	Overall accuracy of flow measurement per meter run shall be better than plus or minus 1 % of the flow rate.