SPS-6 	Specification of Flow Computers

# SCHEDULE SPS-6

PROJECT SPECIFICATION FOR FLOW COMPUTERS

TABLE OF CONTENTS

1.0	SCOPE OF WORK.

2.0	CODES, STANDARDS, AND COMPANY’s SPECIFICATIONS.

3.0	GENERAL - FLOW COMPUTERS - ORIFICE METER RUNS.

4.0	FLOW COMPUTER.

1.0	SCOPE OF WORK.

This specification is intended to define the minimum requirements for flow computers for the Arab Gas Pipeline project Phase II.

2.0	CODES, STANDARDS AND COMPANY's SPECIFICATIONS.

2.1	The latest edition of the following codes or industry standards shall be utilized.

-	International Standard ISO 5167.

2.2	The following Company Specifications shall be utilized:

-	Schedule L

3.0	GENERAL

3.1	The flow computers shall be used to perform flow calculations in accordance with ISO 5167 for gas flow measurements by means of orifice plates with flange tapping.

3.2	The flow computers shall be installed in a flow cabinet.

3.3	Each orifice meter run shall be equipped with two high range differential pressure transmitters (smart type) and one low range differential pressure transmitter (smart type) to give a flow measurement turn down ratio of 4:1. One of the high ranges, differential pressure transmitters shall be used as pay meter, the other as check meter.

3.4	A separate flow computer shall be provided for each meter run.

4.0	FLOW COMPUTER.

4.1	The flow computer shall be a standard manufactured item whose functions and programming is especially for flow measurement by orifice meters. It must be designed to read differential pressure, temperature, pressure and density. From these data and other Operator entered data, the flow computer shall work out the uncorrected and corrected volumes according to ISO 5167.

4.2	The flow computer shall be microprocessor based and shall have a front keyboard and a LCD display to be used for entering new data, selecting displays or giving commands. There shall be a key or keyword system to prevent unauthorized modification of parameters and data.

4.3	The flow computer shall accept inputs from three differential pressure transmitters. Switching over between the low range and the high range transmitter used as pay meter shall be automatically and shall include hysterisis to avoid unstable measurement.

A second high range transmitter shall check the pay meter and an alarm shall be given if the deviation between both measurements exceeds a pre-set value.

Facilities shall be provided to display the inputs of both transmitters and manually set the transmitter that shall be used as the pay meter.

4.4	Inputs shall be available for:

-	Differential pressure.

-	Temperature.

-	Pressure.

-	Density.

4.5	Outputs shall be available as minimum for:

-	4-20 mA signals ((for two separate signals presents corrected flow rate (SCM/H) and cumulative value (SCM/D))

-	Uncorrected volume total (CM, cubic meter).

-	Corrected volume total (SCM).

- 	Uncorrected flow rate (CM/H).

-	Corrected flow rate (SCM/H).

-	Pressure, Temperature and density.

- Alarms.

- Etc.

4.6	Each flow computer shall have a re-settable and a non-re-settable electronic counter for both the uncorrected and corrected volume totals. The re-settable counters shall be reset automatically at operator defined times.

4.7	The flow computer must power field transducers and filter input signals to reject unwanted noise.

4.8	The flow computer shall be able to adopt “fallback” values in the event of transducer failure.

4.9	For each flow computer, a ticket printer shall be provided and installed in the control cabinet for automatic and operator requested printing of reports. Automatic printing shall be at operator defined times. Also the flow computers data shall be interfaced to the new constructed DCS system as well as to the Gas Co-Ordination Center  system.

4.10	The flow computer shall have self-checking routines for diagnostic purposes. Alarms shall be available for:

-	Line pressure, line temperature, line density or differential pressure out of range.

-	High range differential pressures transmitters deviation between pay and check transmitters.

-	System failure.

-	Analog input failure.

-	Etc.

4.11	Calculation cycle time shall be better than 5 sec.

4.12	Those functions, which can not be performed by the flow computer itself, must be realized by separate electronic components installed in the control cabinet.

4.13	The flow computer must be powered by 24 VDC. The contents of the flow computer memories shall not be lost in the vent of a failure or interruption of the power supply. The retention time shall be at least 40 days.

4.14	Each flow computer shall communicate with workstation.

4.15	Communications and data transferring to the GCC SCADA system shall be made via the fiber optic cable.